# Bowie State university fine and performing arts center

ASHRAE Standard 62.1-2007 and 90.1-2007 Analysis

Technical Report 1

Zack Lippert – Mechanical

Advisor: Steve Treado

Location: Bowie, MD

Contents

Executive Summary	2

ASHRAE Standard 62.1 Analysis	3

Section 5 Analysis	3

Section 6 Analysis	6

Standard 62.1 Summary	8

ASHRAE Standard 90.1 Analysis	8

Section 5 – Building Envelope	8

Section 6 – Heating, Ventilations, Air Conditioning	9

Section 7 – Service Water Heating	11

Section 8 – Power	11

Standard 90.1 Summary	11

References	12

Appendix A: Typical Minimum Ventilation Rate Calculations	13

# Executive Summary

The purpose of this report is to analyze the Bowie State University Fine and Performing Arts Center’s compliance with ASHRAE Standards 62.1-2007 and 90.1-2007. This building is 123,000 ft2 and will be the new home of the Department of Fine and Performing Arts. The building contains multiple theaters, recital halls, dance studios, workshops, art studios, offices, classrooms and music rooms.

ASHRAE 62.1 is a standard developed to specify minimum ventilation rates and indoor air quality properties to improve the health and comfort levels of the occupants within the building. For this report a heavy emphasis was place one sections 5 and 6. Section 5 has several requirements for acceptable system design and outdoor air intake rates. The Fine and Performing Arts Center was found to be compliant with all of the requirements in this section. Section 6 dictates the procedure for calculating minimum outdoor air intake rates based on zone type, number of occupants, and zone area. After analyzing the HVAC system all of the zones met, and in most cases surpassed, the minimum OA intake rate.

ASHRAE 92.1 is the standard that dictates the minimum requirements for energy efficient buildings.  This standard pertains to building envelope and insulation as well as mechanical and electrical systems in the building. The Bowie State University Fine and Performing Arts Center was found to be compliant with all of the sections analyzed in this report.

This analysis has found the building to be compliant with both ASHRAE Standards 62.1-2007 and ASHRAE 92.1-2007.

# ASHRAE Standard 62.1 Analysis

## Section 5 Analysis

Section 5.1 Natural Ventilation

Mechanical ventilation was used for the building, therefore no natural ventilation was used.

Section 5.2 Ventilation Air Distribution

The Fine and Performing Arts Center was designed with to be adjustable to achieve the minimum ventilation airflow required by Section 6. The commissioning agents and TAB contractor tested these to verify that it was installed properly.

Section 5.3 Exhaust Duct Location

Exhaust ducts carrying harmful or potentially harmful contaminants, such as those from the rest rooms, scenery shop, painting rooms or ceramics studio, are negatively pressurized to 2 in-wg in order to prevent air from leaking into occupied spaces, or other ducts or plenums.

Section 5.4 Ventilation System Controls

The mechanical ventilation systems are connected to a BACnet internetwork and can be manually changed within 10 seconds of being given the command. It also has numerous sensors throughout the building to measure the carbon dioxide PPM to determine if the area needs additional ventilation air.

Section 5.5 Airstream Surfaces

All surfaces for equipment and ducts in the airstreams were designed to be resistant to mold growth and erosion in according to UL 181 and ASTM C 1338.

Section 5.6 Outdoor Air Intakes

The outdoor air supplied to the AHUs comes from the makeup air units located on the roof. Careful attention was taken to make sure the exhaust fans were placed far enough away from the louvered penthouses containing the MAUs in accordance with Table 1 seen below (Table 5-1 in ASHRAE 62.1-2007).

Table 1

The louvers are designed to prevent snow and rain from entering the building and have weather stripping to prevent water penetration around the edges. Also, the louvers have ½ inch square mesh covering the openings to prevent birds from entering.

Section 5.7 Local Capture of Contaminants

All exhaust fans are vented outdoors through exhaust duct. Backdraft dampers are installed at the inlet of the exhaust fans to prevent the exhaust from coming back into the building.

Section 5.8 Combustion Air

Combustion air dampers are driven open anytime a boiler or dual fuel fired domestic water heater is open and exhaust fans remove the combustion products.

Section 5.9 Particulate Matter Removal

The Fine and Performing Arts Center uses filters upstream of cooling coils of MERV 7 when rated in accordance with ASHRAE 52.2.

Section 5.10 Dehumidification Systems

The building set point for relative humidity is 50%. If the sensors indicate that the relative humidity is greater than 50% the cooling coil valve is driven fully open and space temperature is controlled by bypass dampers.

Section 5.11 Drain Pans

The drain pans were designed from single-wall galvanized steel sheets and made 2 inches deep in compliance with ASHRAE 62.1.

Section 5.12 Finned-Tube Coils and Heat Exchangers

Drain pans are located under all appropriate equipment in accordance with section 5.11, but there is no mention in the specs as to finned-tube coil cleaning.

Section 5.13 Humidifiers and Water-Spray Systems

The humidifiers use potable water to humidify the supply air, and the ductwork has been installed in accordance with the manufacturer’s recommendations.

Section 5.14 Access for Inspection, Cleaning and Maintenance

Access is provided to all exchanger surfaces, blowers, motors, and filters in the MAUs through hinged double wall gasketed access doors. All AHU access doors are at least 24 by 60 inches. Also, access doors are located on the ducts throughout the building to allow them to be cleaned, inspected and maintained.

Section 5.15 Building Envelope and Interior Surfaces

The envelope of the building has been weather proofed to prevent liquid from penetrating the building envelope, and all joints have been caulked and weather stripped.  Also, all of the pipes, ducts and other surfaces that are expected to be colder than the surrounding dew point temperature have been properly insulated to prevent condensation.

Section 5.16 Buildings with Attached Parking Garages

This building does not have an attached parking garage.

Section 5.17 Air Classification and Recirculation

The Fine and Performing Arts Center has Class 1 return air coming from classrooms, offices, theatres and the atrium, which can be recirculated. Class 2 air is returned from the rest rooms and is exhausted straight to the roof. The return air from the painting rooms, dying areas and scene shop are class 4 and cannot be recirculated, therefore it is exhausted out the roof.

Section 5.18 Requirements for Buildings Containing ETS Areas and ETS-Free Areas

This building does not have ETS areas.

## Section 6 Analysis

This section of the standard is a prescriptive procedure that determines the required outdoor air intake rates based on application of the zone, occupancy level, and area of the zone.
All of the AHUs for this building meet the minimum outdoor air intake requirements. A sample analysis has been included in Appendix B. The spreadsheet used for those calculations was created using the following equations.

Breathing Zone Outdoor Airflow(Vbz)

Vbz = Rp × Pz + Ra × Az

Where

Az = zone floor area [ft2]

Pz = zone population [people]

Rp = OA flow rate [cfm/person]

Ra = OA flow rate [cfm/ft2]

Zone Outdoor Airflow (Voz)

Voz = Vbz/Ez

Where

Ez = zone air distribution effectiveness (Ez = 1 from table 6-2)

Single Zone Systems (Vot)

Vot = Voz

Primary Outdoor Air Fraction (Zp)

Zp = Voz/Vpz

Where

Vpz = zone primary airflow

Uncorrected Outdoor Air Intake (Vou)

Vou = D∑all zones(Rp × Pz) + ∑all zones(Ra × Az)

Where

D = occupant diversity, which is defined as;

D = Ps/∑all zones Pz

Where

Ps = system population

Outdoor Air Intake(Vot)

Vot = Vou/Ev

## Standard 62.1 Summary

The HVAC equipment and ductwork was all carefully designed to meet the requirements of Section 5. Also, all of the AHUs, VAVs, and FPVs were sized appropriate to allow for more than the minimum ventilation rates throughout each of the zones in the building.

# ASHRAE Standard 90.1 Analysis

## Section 5 – Building Envelope

Section 5.1.4 Climate

The Bowie State University Campus is located in Bowie, MD. According to Figure 1, seen below, this building is in zone 4A. Zone 4A is defined as mixed humid air, with less than 4500 cooling degree days and more than 3600 heating degree days but less than 5400.

Figure 1: ASHRAE Climate Zones

Section 5.2 Compliance Paths

This building is in compliance with the Prescriptive Building Envelope Option because the vertical fenestration area is approximately 30% that of the gross wall area and the skylights are less than 5% of the roof area.

Section 5.4 Mandatory Provisions

All doors intended to be entrances to the building are separated from conditioned spaces by the use of vestibules larger than 7 feet wide. Also, all loading dock doors have been properly sealed with weather stripping.

Section 5.5 Prescriptive Building Envelope Option

Glazing U-factor and insulation R-values were not available, but have been requested and this section will be updated shortly.

## Section 6 – Heating, Ventilations, Air Conditioning

Section 6.2 Compliance Path

There are two options to determine the efficiency of the HVAC systems in a building, the prescriptive path and the simplified approach. The BSU Fine and Performing Arts Center is greater than 25,000 SF and more than two stories, therefore the prescriptive path was chosen.

Section 6.4 Mandatory Provisions

This section provides minimum energy efficiencies that HVAC equipment must meet. Table 2 below shows the required and the actual equipment efficiencies for the types of HVAC equipment in the building. As you can see the equipment meets the 90.1 Standards.

| Equipment | Size | 90.1 Minimum Efficiency | Equipment Efficiency | Compliance |
| --- | --- | --- | --- | --- |
| Air-cooled Chiller | 305 tons | 2.80 COP | 3.14 COP | YES |
| Gas-Fired Boiler (2) | 1,712 MBH | 80% | 81.5% | YES |

Table 2

Section 6.5 Prescriptive Path

The fans for the building must not exceed the limits in Table 6.5.3.1.1A of Standard 90.1. The calculations for these fans have been included below in Table 3. The majority of the fans do not exceed the power limits, however 4 do exceed, however two of them are less than 1 HP and one is for a fume hood, therefore are exempt from power limitation calculation.

| Fan | HP | CFM | CFM×.0011 | Compliance |
| --- | --- | --- | --- | --- |
| EF-1 | 0.17 | 235 | 0.2585 | Yes |
| EF-2 | 0.25 | 800 | 0.88 | Yes |
| EF-3 | 0.33 | 1650 | 1.815 | Yes |
| EF-4 | 0.25 | 480 | 0.528 | Yes |
| EF-5 | 0.17 | 370 | 0.407 | Yes |
| EF-6 | 0.50 | 2250 | 2.475 | Yes |
| EF-7 | 1.50 | 2760 | 3.036 | Yes |
| EF-8 | 0.75 | 2880 | 3.168 | Yes |
| EF-9 | 0.17 | 150 | 0.165 | No |
| EF-11 | 0.17 | 220 | 0.242 | Yes |
| EF-12 | 0.17 | 280 | 0.308 | Yes |
| EF-13 | 0.17 | 400 | 0.44 | Yes |
| EF-14 | 0.25 | 800 | 0.88 | Yes |
| EF-15 | 0.50 | 500 | 0.55 | Yes |
| EF-16 | 0.17 | 400 | 0.44 | Yes |
| EF-17 | 0.50 | 500 | 0.55 | Yes |
| EF-18 | 0.33 | 1400 | 1.54 | Yes |
| EF-19 | 2.00 | 1500 | 1.65 | No |
| EF-20 | 0.25 | 900 | 0.99 | Yes |
| EF-21 | 0.17 | 150 | 0.165 | No |
| EF-22 | 0.33 | 4500 | 4.95 | Yes |
| EF-23 | 0.25 | 2000 | 2.2 | Yes |
| EF-24 | 0.50 | 3000 | 3.3 | Yes |
| EF-25 | 0.25 | 1500 | 1.65 | Yes |
| EF-26 | 0.17 | 400 | 0.44 | Yes |
| EF-27 | 0.17 | 400 | 0.44 | Yes |
| EF-28 | 0.17 | 400 | 0.44 | Yes |
| EF-29 | 0.75 | 8000 | 8.8 | Yes |
| EF-30 | 0.17 | 400 | 0.44 | Yes |
| EF-31 | 0.20 | 312 | 0.3432 | Yes |
| RF-4 | 7.50 | 5000 | 5.5 | No |
| RF-5 | 1.50 | 3500 | 3.85 | Yes |
| RF-6 | 0.50 | 1800 | 1.98 | Yes |

Table 3: Fan Power Limitations

The building has 3 MAUs, all of which have enthalpy wheels to recover energy from the exhaust air before it is released. AHU-4 also has an enthalpy wheel for energy recovery purposes. All of these units are required to be at least 50% effective in energy recovery, all four enthalpy wheels exceed this requirement.

Section 6.7 Submittals

The HVAC Systems have all been balanced, tested and commissioned after being installed, and O&M manuals have been provided to the owner for continued energy efficient performance through the operation of the building.

## Section 7 – Service Water Heating

This section requires that all hot water gas and oil supply boilers have a minimum of 80% efficiency. The Fine and Performing Arts Center has one boiler with an efficiency of 81.5%, which meets the standard.

## Section 8 – Power

The BSU Fine and Performing Arts Center’s electrical power distribution is sized so that the feeder conductors have a voltage drop of less than 2% and the branch circuit conductors have a voltage drop of less than 3% at design load. Both of those voltage drops are lower than the maximum allowed drops by this section.

## Standard 90.1 Summary

Energy efficiency was important throughout the design, construction and life of the building. Therefore great effort was put into creating an energy efficient building. The building conforms to the various requirements of ASHRAE Standard 90.1-2007.

# References

ASHRAE.2007, ANSI/ASHRAE, Standard 62.1-2007, Ventilation for Acceptable Indoor Air Quality. American Society of Heating Refrigeration and Air-Conditioning Engineer, Inc. Atlanta, GA.

ASHRAE.2007, ANSI/ASHRAE, Standard 90.1-2007, Energy Standard for Building Except Low-Rise Residential Buildings. American Society of Heating Refrigeration and Air-Conditioning Engineers, Inc. Atlanta, GA.

EYP Architecture & Engineering, P.C. Architectural Construction Documents. EYP Architecture & Engineering, Washington D.C.

EYP Architecture & Engineering, P.C. Electrical Construction Documents. EYP Architecture & Engineering, Washington D.C.

EYP Architecture & Engineering, P.C. Mechanical Construction Documents. EYP Architecture & Engineering, Washington D.C.

Appendix A: Typical Minimum Ventilation Rate Calculations